3/30/2025 9:00:36 PM			
			
Fluke Energy Analyze Report		
Client:		

Location:		

Description:		

Apex Kemps Creek.fca		page 1 of 9	

3/30/2025 9:00:36 PM			

Session name:		
ES.011	
	
Session UUID:		
	bd2a38d6-56c1-4a6f-9261-dfc4cc7e8262		
			
Description:			

Notes:			

Study Type:			
	Energy study		
			
Measurement Mode:			

Topology:			
	3-ph Wye		
			
Nominal Voltage:			
	 400V		
			
Nominal Frequency:			
	 50Hz		
			
Buffer Type:			
	linear (do not overwrite)		
			
Start and End Dates:			
	Configured start: 10/16/2021 5:49:49 AM		
	Configured end: 10/23/2021 5:49:49 AM		
			
	Actual start: 10/16/2021 5:49:49 AM		
	Actual end: 10/23/2021 5:49:49 AM		
			
Duration:			
	Configured duration: 7d 0h 0m 0s		
	Actual duration: 7d 0h 0m 0s		
			
Number of averaging intervals:			
	Number of trend intervals as configured: 120959		
	Number of trend intervals as present: 120961		
	Trend interval length: 5sec		
	Number of demand intervals as configured: 2015		
	Number of demand intervals as present: 2017		
	Demand interval: 5min		
	Number of PQ intervals as configured: 1007		
	Number of PQ intervals as present: 1007		
	PQ interval length: 10min		
			
Event limits:			
	Dip:  90%		
			
	Swell:  110%		
			
	Interruption:  5%		
			
	Hysteresis:  2%		
			
	Inrush current: - - -			
				
	Rapid Voltage Changes: - - -			
				
Apex Kemps Creek.fca		page 2 of 9	

3/30/2025 9:00:36 PM			

	Waveform Deviation: - - -		
			
	Mains signalling voltage limit: - - -		
			
	Sliding Reference:  Off		
			
Event:		
	Events recorded: 4		
			
			Phase L1	Phase L2	Phase L3	Neutral	Combined events			
		Dip	1	1	1		1			
		Swell	0	0	0		0			
		Interruption	0	0	0		0			
		Inrush Current	0	0	0	0				
		Waveshape Deviation	0	0	0					
					
	Waveform recordings: 1		
			
	RMS recordings: 1		
			
	MSV recordings: 0		
			
Instrument information:			
Instrument Type:	FLUKE 1738			
Installed Licenses:	none			
Instrument versions:	Firmware Version:  2.2			
			
	DSP Version:  2.7			
Instrument Serial Number:	50233819			
Instrument UUID:	e11b6c87-af78-4c46-94be-d2d1eb3f11de			
Instrument time zone:	Australia/Sydney			
Instrument name:	FLUKE1738<50233819>			
			
Attached Current Sensors:			
			
	Channel	Ratio	Model	Range	Serial No				
	1 - L1	1:1	iFlex1500-12	1500A	495471026				
	2 - L2	1:1	iFlex1500-12	1500A	495471032				
	3 - L3	1:1	iFlex1500-12	1500A	495471021				
	4 - N	1:1	iFlex1500-12	1500A	495471020				
					
Voltage mapping:			
			
	Channel	Ratio				
	1 - L1	1:1				
	2 - L2	1:1				
	3 - L3	1:1				
					
Aux Settings:			
			
	Channel	Gain	Offset	Unit				
	Aux1	1	0	V				
	Aux2	1	0	V				
					
Apex Kemps Creek.fca		page 3 of 9	

3/30/2025 9:00:37 PM			
			
Evaluated session	Begin	End		
ES.011	10/16/2021 5:49:49 AM	10/23/2021 5:49:49 AM		
		
Summary		
	Frequency	PASS		
	Slow Voltage Variations	FAIL		
	Voltage Harmonics	FAIL		
	Unbalance	PASS		
	Flicker Plt	(not measured)		
	Mains Signaling Voltage	(not measured)		
	Result	FAIL		
			
Frequency			
	Required values within limit	99.5% / 100% of the time, according to EN50160:2010		
	Maximum 99.5% / 100%	+1% / +4% of 50 Hz		
	Minimum 99.5% / 100%	-1% / -6% of 50 Hz		
			
	Results		
	99.5% Value	100% Value			
Result	PASS	PASS			
% Within Limit	100.00%	100.00%			
Maximum 99.5% / 100%	50.06Hz
(0.12%)	50.08Hz
(0.16%)			
Time		10/18/2021
14:43:20			
Minimum 99.5% / 100%	49.94Hz
(-0.12%)	49.86Hz
(-0.28%)			
Time		10/18/2021
15:43:00			
			
Slow Voltage Variations			
	Required values within limit	95% / 100% of the time, according to EN50160:2010			
	Maximum 95% / 100%	+10% / +10% of 400 V			
	Minimum 95% / 100%	-10% / -15% of 400 V			
				
	Results		
	95% Value	100% Value			
	L1N	L2N	L3N	L1N	L2N	L3N			
Result	FAIL	FAIL	FAIL	FAIL	FAIL	FAIL			
% Within Limit	0.00%	0.00%	0.00%	0.00%	0.00%	0.00%			
Maximum 95% / 100%	249.21V
(-37.70%)	248.57V
(-37.86%)	245.41V
(-38.65%)	249.21V
(-37.70%)	248.57V
(-37.86%)	245.41V
(-38.65%)			
Time				10/20/2021
12:30:00	10/17/2021
08:10:00	10/22/2021
03:30:00			
Minimum 95% / 100%	239.95V
(-40.01%)	238.33V
(-40.42%)	233.83V
(-41.54%)	236.98V
(-40.76%)	235.63V
(-41.09%)	227.42V
(-43.14%)			
Time				10/19/2021
15:40:00	10/21/2021
18:00:00	10/19/2021
17:00:00			
			
Apex Kemps Creek.fca		page 4 of 9	

3/30/2025 9:00:37 PM			

Voltage Harmonics		
	Required values within limit	95% of the time, according to EN50160:2010		
	h21 95%	0.5%		
			
	Results		
		95% Value	Maximum Value			
		L1N	L2N	L3N	L1N	L2N	L3N			
h21	Result	FAIL	FAIL	FAIL						
	% Within Limit	87.39%	94.74%	91.36%						
	Value	1.11%	0.50%	0.73%	1.95%	0.80%	1.24%			
	Time				10/23/2021
00:40:00	10/17/2021
09:10:00	10/17/2021
01:40:00			
			
Unbalance			
	Required values within limit	95% of the time, according to EN50160:2010			
	Maximum 95%	2%			
				
	Results		
	95% Value	Maximum Value			
Result	PASS				
% Within Limit	100.00%				
Value	0.85%	1.11%			
Time		10/20/2021 9:00:00 AM			
			
Events Summary			
	Number of events	1		
			
Apex Kemps Creek.fca		page 5 of 9	

3/30/2025 9:00:37 PM			
			
DisDIP Table		
	Interrupt		
			
		Duration			
		t ≤ 180s	180s < t			
	5% > u
(20V > u)					
	Swell		
			
		Duration			
		t < 10ms	10ms ≤ t ≤ 500ms	500ms < t ≤ 5s	5s < t ≤ 60s	60s < t			
	u ≥ 120%
(u ≥ 480V)								
	120% > u > 110%
(480V > u > 440V)								
	110% ≥ u
(440V ≥ u)								
				
	Dip		
			
		Duration			
		t < 10ms	10ms ≤ t ≤ 200ms	200ms < t ≤ 500ms	500ms < t ≤ 1s	1s < t ≤ 5s	5s < t ≤ 60s	60s < t			
	u ≥ 90%
(u ≥ 360V)										
	90% > u ≥ 80%
(360V > u ≥ 320V)										
	80% > u ≥ 70%
(320V > u ≥ 280V)										
	70% > u ≥ 40%
(280V > u ≥ 160V)							1			
	40% > u ≥ 5%
(160V > u ≥ 20V)										
	5% > u
(20V > u)										
				
	EN 50160 classification				
					
Apex Kemps Creek.fca		page 6 of 9	

3/30/2025 9:00:37 PM			
			
	Voltage Harmonics limit evaluation		
	Nominal Voltage	400 V			
	Nominal Frequency	50 Hz			
	Required values within limit	95% of the time, according to EN50160:2010			
				
	Phase L1N		
	95% Value	Maximum Value			
	Limit	Result	Value	% Within Limit	Value	Time			
THD[40]	8%	PASS	2.15%	100.00%	2.86%	10/17/2021 1:10:00 AM			
h02	2%	PASS	0.07%	100.00%	0.08%	10/23/2021 4:40:00 AM			
h03	5%	PASS	1.14%	100.00%	1.37%	10/21/2021 6:10:00 AM			
h04	1%	PASS	0.05%	100.00%	0.06%	10/18/2021 5:50:00 PM			
h05	6%	PASS	0.77%	100.00%	0.88%	10/17/2021 4:30:00 AM			
h06	0.5%	PASS	0.03%	100.00%	0.04%	10/18/2021 5:50:00 PM			
h07	5%	PASS	1.30%	100.00%	1.38%	10/16/2021 7:10:00 PM			
h08	0.5%	PASS	0.05%	100.00%	0.06%	10/17/2021 1:50:00 PM			
h09	1.5%	PASS	0.59%	100.00%	0.73%	10/22/2021 1:50:00 PM			
h10	0.5%	PASS	0.03%	100.00%	0.04%	10/18/2021 6:20:00 PM			
h11	3.5%	PASS	0.70%	100.00%	0.80%	10/16/2021 6:40:00 AM			
h12	0.5%	PASS	0.03%	100.00%	0.04%	10/23/2021 2:40:00 AM			
h13	3%	PASS	0.43%	100.00%	0.59%	10/19/2021 6:20:00 PM			
h14	0.5%	PASS	0.08%	100.00%	0.10%	10/17/2021 1:30:00 PM			
h15	0.5%	PASS	0.27%	100.00%	0.38%	10/17/2021 10:30:00 AM			
h16	0.5%	PASS	0.05%	100.00%	0.07%	10/16/2021 6:20:00 AM			
h17	2%	PASS	0.59%	100.00%	0.67%	10/22/2021 5:20:00 PM			
h18	0.5%	PASS	0.06%	100.00%	0.13%	10/23/2021 2:40:00 AM			
h19	1.5%	PASS	0.58%	100.00%	0.88%	10/23/2021 12:40:00 AM			
h20	0.5%	PASS	0.14%	100.00%	0.24%	10/18/2021 1:40:00 AM			
h21	0.5%	FAIL	1.11%	87.39%	1.95%	10/23/2021 12:40:00 AM			
h22	0.5%	PASS	0.10%	100.00%	0.16%	10/23/2021 12:40:00 AM			
h23	1.5%	PASS	0.17%	100.00%	0.28%	10/22/2021 10:10:00 PM			
h24	0.5%	PASS	0.06%	100.00%	0.10%	10/16/2021 6:20:00 AM			
h25	1.5%	PASS	0.18%	100.00%	0.30%	10/17/2021 1:40:00 AM			
			
Apex Kemps Creek.fca		page 7 of 9	

3/30/2025 9:00:37 PM			

	Phase L2N		
	95% Value	Maximum Value			
	Limit	Result	Value	% Within Limit	Value	Time			
THD[40]	8%	PASS	1.93%	100.00%	2.15%	10/20/2021 7:20:00 AM			
h02	2%	PASS	0.12%	100.00%	0.13%	10/23/2021 5:10:00 AM			
h03	5%	PASS	1.14%	100.00%	1.23%	10/20/2021 7:20:00 AM			
h04	1%	PASS	0.05%	100.00%	0.06%	10/20/2021 6:40:00 PM			
h05	6%	PASS	0.52%	100.00%	0.65%	10/17/2021 4:20:00 AM			
h06	0.5%	PASS	0.03%	100.00%	0.05%	10/20/2021 6:40:00 PM			
h07	5%	PASS	1.29%	100.00%	1.38%	10/16/2021 8:20:00 PM			
h08	0.5%	PASS	0.04%	100.00%	0.04%	10/22/2021 6:30:00 AM			
h09	1.5%	PASS	0.56%	100.00%	0.70%	10/18/2021 5:20:00 PM			
h10	0.5%	PASS	0.03%	100.00%	0.03%	10/17/2021 6:00:00 PM			
h11	3.5%	PASS	0.61%	100.00%	0.71%	10/17/2021 6:30:00 AM			
h12	0.5%	PASS	0.03%	100.00%	0.04%	10/22/2021 7:00:00 AM			
h13	3%	PASS	0.49%	100.00%	0.76%	10/20/2021 7:50:00 AM			
h14	0.5%	PASS	0.03%	100.00%	0.05%	10/20/2021 6:10:00 PM			
h15	0.5%	PASS	0.34%	99.90%	0.51%	10/19/2021 5:00:00 PM			
h16	0.5%	PASS	0.04%	100.00%	0.05%	10/22/2021 1:40:00 AM			
h17	2%	PASS	0.59%	100.00%	0.90%	10/16/2021 6:50:00 PM			
h18	0.5%	PASS	0.04%	100.00%	0.07%	10/16/2021 6:20:00 AM			
h19	1.5%	PASS	0.41%	100.00%	0.61%	10/16/2021 6:20:00 AM			
h20	0.5%	PASS	0.06%	100.00%	0.11%	10/16/2021 6:20:00 AM			
h21	0.5%	FAIL	0.50%	94.74%	0.80%	10/17/2021 9:10:00 AM			
h22	0.5%	PASS	0.05%	100.00%	0.08%	10/19/2021 1:40:00 AM			
h23	1.5%	PASS	0.15%	100.00%	0.23%	10/17/2021 1:40:00 AM			
h24	0.5%	PASS	0.03%	100.00%	0.05%	10/23/2021 12:40:00 AM			
h25	1.5%	PASS	0.13%	100.00%	0.17%	10/19/2021 7:10:00 PM			
			
Apex Kemps Creek.fca		page 8 of 9	

3/30/2025 9:00:37 PM			

	Phase L3N		
	95% Value	Maximum Value			
	Limit	Result	Value	% Within Limit	Value	Time			
THD[40]	8%	PASS	2.57%	100.00%	2.99%	10/20/2021 4:50:00 PM			
h02	2%	PASS	0.06%	100.00%	0.10%	10/17/2021 7:50:00 AM			
h03	5%	PASS	2.12%	100.00%	2.51%	10/20/2021 4:50:00 PM			
h04	1%	PASS	0.04%	100.00%	0.06%	10/20/2021 4:50:00 PM			
h05	6%	PASS	0.95%	100.00%	1.09%	10/17/2021 3:30:00 AM			
h06	0.5%	PASS	0.04%	100.00%	0.05%	10/19/2021 6:40:00 AM			
h07	5%	PASS	1.09%	100.00%	1.24%	10/20/2021 8:50:00 AM			
h08	0.5%	PASS	0.04%	100.00%	0.05%	10/18/2021 9:30:00 AM			
h09	1.5%	PASS	0.38%	100.00%	0.52%	10/22/2021 2:40:00 PM			
h10	0.5%	PASS	0.03%	100.00%	0.04%	10/16/2021 8:50:00 AM			
h11	3.5%	PASS	0.52%	100.00%	0.63%	10/17/2021 11:00:00 AM			
h12	0.5%	PASS	0.04%	100.00%	0.05%	10/20/2021 12:20:00 PM			
h13	3%	PASS	0.59%	100.00%	0.80%	10/16/2021 9:10:00 AM			
h14	0.5%	PASS	0.05%	100.00%	0.07%	10/20/2021 10:50:00 AM			
h15	0.5%	FAIL	0.50%	94.04%	0.69%	10/21/2021 6:00:00 AM			
h16	0.5%	PASS	0.04%	100.00%	0.05%	10/18/2021 7:30:00 AM			
h17	2%	PASS	0.24%	100.00%	0.33%	10/21/2021 6:10:00 AM			
h18	0.5%	PASS	0.05%	100.00%	0.09%	10/17/2021 1:40:00 AM			
h19	1.5%	PASS	0.27%	100.00%	0.41%	10/17/2021 6:10:00 AM			
h20	0.5%	PASS	0.08%	100.00%	0.14%	10/17/2021 6:10:00 AM			
h21	0.5%	FAIL	0.73%	91.36%	1.24%	10/17/2021 1:40:00 AM			
h22	0.5%	PASS	0.06%	100.00%	0.12%	10/23/2021 12:40:00 AM			
h23	1.5%	PASS	0.18%	100.00%	0.28%	10/17/2021 6:10:00 AM			
h24	0.5%	PASS	0.05%	100.00%	0.07%	10/17/2021 6:10:00 AM			
h25	1.5%	PASS	0.12%	100.00%	0.16%	10/20/2021 4:50:00 PM			
			
Apex Kemps Creek.fca		page 9 of 9